How to connect sub module DS-K2M002X of DS-K270X controller with face terminal

Preparation

| Type | Model | Version |
| --- | --- | --- |
| Software | IVMS-4200 or HCP or HCAC |  |
| Access Control Terminal | DS-K270X |  |
| Card reader | DS-K1T341CM |  |

How to connect sub module DS-K2M002X of DS-K270X controller with face terminal

Introduction: This article will introduce how to connect sub module DS-K2M002X of DS-K270X controller with face terminal.

- Wiring

- Set the first access module 485 address is 1 corresponded dip switch 1000 0000, and 485A of access module connect to 485A of main controller.

- Face terminal connect to 485C of access module.

- Configuration

- Login the DS-K2704X web.

- Add access module, make sure your module have connect to main access controller.

- And then you can find your access module have been online

- Login the face terminal web, if you want to control door 5, set 485 address is 1.

- Check this card reader whether it is online, as shown below.

- Test

- Create a person on web of access controller and face terminal. You can also use IVMS-4200 to apply the access level.

- Swipe face to test, you can find the door5 is unlocked.

Note:

- The access module can connect four card readers via 485 communication, address 1 and 2 open the door 1; address 3 and 4 open the door 2. The 485 address represented by the DIP switch of the card reader as show below. After the configuration is complete, the card reader needs to restarted.

- 1000 0000 - >1

- 0100 0000 - >2

- 1100 0000 - >3

- 0010 0000 - >4

- About 485 Wiring of card reader, we recommend to use 485C interface, because it is the main communication of the card reader, and 485D is a redundancy interface.

- If you want to connect 485D interface of access module, you need check whether enable RS-485 communication backup.